## Sheet1
project | phase | zone | discipline | system_trade | work_package_dfow | work_sequence_no | submission_category | document_code | submission_title | mandatory | spec_section | drawing_ref | code_standard_ref | vendor_manufacturer | hold_witness_review | acceptance_criteria | tolerance_limit | required_before | responsible_org | reviewer | planned_submission_date | actual_submission_date | review_status | review_cycle_count | final_approval_date | linked_evidence | related_ncr_no | retest_required | gate | closeout_status | remarks
Luxury Hotel QAQC | P01 Earthwork | All | Civil | Survey | Control points benchmark verification | EW-001 | TEST | TST-EW-001 | Survey benchmark and control network verification | Yes | 01 71 23 | CIV-SURV-001 | Project Survey Spec | Survey Team | Witness | Control points established and signed | ±5mm | Excavation start | Main Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | No | G1 | Open | Prerequisite for all setting out
Luxury Hotel QAQC | P01 Earthwork | All | Civil | Earthworks | Excavation and shoring | EW-002 | MS | MS-EW-001 | Excavation and shoring method statement | Yes | 31 23 00 | CIV-EW-101 | Project Spec + Local Code | N/A | Review | Approved MS with sequence and safety controls | N/A | Excavation start | Main Contractor | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G1 | Open
Luxury Hotel QAQC | P01 Earthwork | All | Civil | Earthworks | Backfill source approval | EW-003 | MIR | MIR-EW-001 | Backfill material approval and source validation | Yes | 31 23 23 | CIV-EW-201 | ASTM D698/D1557 | Approved Quarry | Review | Approved source + certificates | N/A | Delivery to site | Main Contractor | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G1 | Open
Luxury Hotel QAQC | P01 Earthwork | All | Civil | Earthworks | Compaction verification | EW-004 | TEST | TST-EW-002 | Field density compaction tests | Yes | 31 23 23 | CIV-EW-202 | ASTM D6938 | 3rd Party Lab | Witness | Compaction meets project requirement | As per spec % | Layer closure | Contractor + Lab | QAQC + Consultant |  |  |  |  | 0 |  |  |  | Yes | G4 | Open
Luxury Hotel QAQC | P01 Earthwork | Basement | MEP | Underground Services | Underground sleeves and utilities as-built capture | EW-005 | DOC | DOC-EW-001 | Underground MEP and utility pre-backfill as-built | Yes | 01 78 39 | MEP-UG-001 | Project ER | N/A | Hold | All buried services recorded and approved | N/A | Backfilling | MEP Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | No | G3 | Open | Commonly missed
Luxury Hotel QAQC | P02 Shell&Core | Tower A | Structural | Concrete | Formwork and rebar pre-pour readiness | SC-001 | ITP | ITP-SC-001 | Concrete frame ITP with hold points | Yes | 03 30 00 | STR-CON-001 | ACI/BS EN | N/A | Hold | No pour without signed pre-pour checklist | Cover as spec | Concrete pour | Main Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | No | G2 | Open
Luxury Hotel QAQC | P02 Shell&Core | Tower A | Structural | Rebar | Rebar and coupler approval | SC-002 | MIR | MIR-SC-001 | Rebar and coupler material approval | Yes | 03 20 00 | STR-REB-001 | ASTM A615/A706 | Approved Mill | Review | Mill cert + approved lab tests | N/A | Installation | Main Contractor | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G1 | Open
Luxury Hotel QAQC | P02 Shell&Core | Tower A | Structural | Concrete | Pour and sampling controls | SC-003 | TEST | TST-SC-001 | Slump and compressive strength tests | Yes | 03 30 00 | STR-CON-002 | ASTM C143/C39 | Approved Supplier | Witness | Strength class achieved | As design | Formwork stripping | Lab + Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | Yes | G4 | Open
Luxury Hotel QAQC | P02 Shell&Core | All | Architectural | Masonry | Blockwork and mortar control | SC-004 | MS | MS-SC-002 | Masonry installation method statement | Yes | 04 20 00 | ARC-MAS-001 | BS EN 771 | N/A | Review | Approved sequence incl. ties/openings | N/A | Blockwork start | Main Contractor | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G1 | Open | Previously missing trade
Luxury Hotel QAQC | P02 Shell&Core | All | MEP | Builders Work | MEP sleeve opening builder's work coordination | SC-005 | ITP | ITP-SC-002 | Builder's work and embedded item ITP | Yes | 23/26/28 Div | MEP-BW-001 | Project Spec | N/A | Hold | No unauthorized core cuts post-pour | As drawings | Concrete pour and wall closure | MEP + Civil | QAQC + Consultant |  |  |  |  | 0 |  |  |  | No | G2 | Open | Frequent rework item
Luxury Hotel QAQC | P02 Shell&Core | Facade | Architectural | Facade Anchors | Facade embed and anchor setting out | SC-006 | MS | MS-SC-003 | Facade anchor embed method statement | Yes | 08 44 13 | FCD-EMB-001 | Facade Spec | Nominated Facade | Hold | Embed coordinates and pullout compliance | ±3mm | Slab edge closure | Facade Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | No | G3 | Open | Luxury tower critical
Luxury Hotel QAQC | P03 Fitout | Guestroom | Architectural | Mockup | Guestroom mockup and sample board approvals | FO-001 | DOC | DOC-FO-001 | Mockup room approval records | Yes | 01 43 39 | ARC-MKU-001 | Project Spec + Brand Standard | N/A | Hold | Mockup signed by client/consultant/operator | N/A | Mass fitout start | Main Contractor | Client + Consultant |  |  |  |  | 0 |  |  |  | No | G3 | Open | Commonly forgotten for hotels
Luxury Hotel QAQC | P03 Fitout | Guestroom | Architectural | Drywall/Ceiling | Partition and ceiling method statement | FO-002 | MS | MS-FO-001 | Drywall and gypsum ceiling installation MS | Yes | 09 29 00 | ARC-GYP-001 | ASTM C840 | N/A | Review | Approved sequence and access panel coordination | N/A | Partition works start | Main Contractor | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G1 | Open | Previously missing trade
Luxury Hotel QAQC | P03 Fitout | Guestroom | Architectural | Floors | Stone/tile dry-lay approval | FO-003 | DOC | DOC-FO-002 | Stone and tile dry-lay approval minutes | Yes | 09 30 00 | ARC-TIL-001 | Project Finishes Spec | Supplier | Witness | Pattern | tone and joints approved | Joint width as spec | Mass tiling | Main Contractor | Consultant + Client |  |  |  |  | 0 |  |  |  | No | G3 | Open
Luxury Hotel QAQC | P03 Fitout | Wet Areas | Architectural | Waterproofing | Wet area waterproofing and flood test | FO-004 | TEST | TST-FO-001 | Wet area flood testing report | Yes | 07 14 16 | ARC-WPF-001 | Project Spec | N/A | Hold | No leakage after hold period | N/A | Tiling and closure | Contractor + QAQC | Consultant |  |  |  |  | 0 |  |  |  | Yes | G4 | Open
Luxury Hotel QAQC | P03 Fitout | Guestroom | MEP | Concealed MEP | Pre-close MEP inspections and tests | FO-005 | TEST | TST-FO-002 | Pre-close pressure/continuity/insulation tests | Yes | 23/26 Div | MEP-CLS-001 | IEC/ASHRAE/NFPA | N/A | Hold | All concealed services tested and signed | As spec | Ceiling and shaft closure | MEP Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | Yes | G4 | Open
Luxury Hotel QAQC | P03 Fitout | Kitchen | MEP | Public Health | Grease waste and kitchen utility testing | FO-006 | TEST | TST-FO-003 | Kitchen drainage and grease system test report | Yes | 22 13 00 | MEP-KIT-001 | Local Code + Spec | N/A | Witness | No leaks; slope and cleanout compliance | As spec | Kitchen close-up | MEP Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | Yes | G4 | Open | Hotel-specific critical
Luxury Hotel QAQC | P03 Fitout | BOH | MEP | Firestopping | Shaft and riser firestopping closure checks | FO-007 | ITP | ITP-FO-001 | Firestopping inspection and closure ITP | Yes | 07 84 00 | FIR-STP-001 | UL/EN listings | Approved System | Hold | No unsealed penetrations before closure | As listing | Ceiling and shaft closure | Main Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | No | G2 | Open | Often missed
Luxury Hotel QAQC | P03 Fitout | Public Areas | Architectural | Special Finishes | Special finishes (stone/wood/metal) MS and approvals | FO-008 | MS | MS-FO-002 | Special finishes installation method statement | Yes | 09 90 00 | ARC-FIN-001 | Project Spec | Nominated Supplier | Review | Mockup and substrate acceptance complete | N/A | Installation | Main Contractor | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G1 | Open | Luxury quality driver
Luxury Hotel QAQC | P04 Snag | All | All | Snagging | Snag categorization and rectification workflow | SN-001 | DOC | DOC-SN-001 | Snag register and closure protocol | Yes | 01 77 00 | QA-SNG-001 | Project QA Plan | N/A | Review | Priority and SLA by severity agreed | N/A | Snag closure start | Main Contractor | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G3 | Open
Luxury Hotel QAQC | P04 Snag | All | All | Snagging | Reinspection and closure verification | SN-002 | TEST | TST-SN-001 | Snag reinspection closure records | Yes | 01 77 00 | QA-SNG-002 | Project QA Plan | N/A | Witness | Major/critical snag zero before T&C | N/A | Phase handover to T&C | QAQC + Contractor | Consultant + Client |  |  |  |  | 0 |  |  |  | Yes | G4 | Open
Luxury Hotel QAQC | P05 Test&Commissioning | All | MEP | Commissioning | Commissioning strategy and sequences | TC-001 | MS | MS-TC-001 | System-wise commissioning method statement | Yes | 01 91 00 | MEP-CX-001 | ASHRAE/CIBSE/NFPA | N/A | Review | Approved sequence and roles | N/A | Pre-commissioning start | Commissioning Team | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G1 | Open
Luxury Hotel QAQC | P05 Test&Commissioning | All | MEP | Instrumentation | Test instruments calibration validity | TC-002 | MIR | MIR-TC-001 | Calibration certificates for all test instruments | Yes | 01 40 00 | MEP-CAL-001 | ISO 9001 7.1.5 / ISO 17025 | Accredited Lab | Hold | All certs valid and traceable | N/A | Any functional/performance test | Commissioning Team | QAQC Manager |  |  |  |  | 0 |  |  |  | No | G1 | Open
Luxury Hotel QAQC | P05 Test&Commissioning | All | MEP | HVAC | TAB and functional performance tests | TC-003 | TEST | TST-TC-001 | TAB and FPT records | Yes | 23 05 93 | MEP-HVAC-001 | ASHRAE/NEBB | TAB Agency | Witness | Design air/water flow and controls pass | As design | System acceptance | Commissioning Team | QAQC + Consultant |  |  |  |  | 0 |  |  |  | Yes | G4 | Open
Luxury Hotel QAQC | P05 Test&Commissioning | All | MEP | Life Safety | Fire alarm cause and effect integrated test | TC-004 | TEST | TST-TC-002 | Fire alarm/BMS/lift/PA integrated C&E test | Yes | 28 31 00 | FLS-INT-001 | NFPA 72 + Local Fire Code | N/A | Hold | All matrix scenarios pass | N/A | Authority/client witness | Commissioning Team | QAQC + AHJ |  |  |  |  | 0 |  |  |  | Yes | G4 | Open | Hotel life safety critical
Luxury Hotel QAQC | P05 Test&Commissioning | All | MEP | Power | Emergency power and load shedding tests | TC-005 | TEST | TST-TC-003 | Generator ATS and load shedding tests | Yes | 26 32 13 | ELC-EMG-001 | IEC + Project Spec | N/A | Witness | All failover scenarios pass | N/A | IST completion | Commissioning Team | QAQC + Consultant |  |  |  |  | 0 |  |  |  | Yes | G4 | Open
Luxury Hotel QAQC | P05 Test&Commissioning | All | ELV | Security/ELV | ELV integration and interface tests | TC-006 | TEST | TST-TC-004 | Access/CCTV/BMS interface test records | Yes | 28 Div | ELV-INT-001 | Project ELV Spec | N/A | Review | All required interfaces validated | N/A | Client soft opening | ELV Contractor | QAQC + Operator |  |  |  |  | 0 |  |  |  | Yes | G4 | Open | Often late-discovered
Luxury Hotel QAQC | P06 Handover | All | All | Handover | As-built and redline completeness | HD-001 | DOC | HDO-001 | Final as-built drawing register and approvals | Yes | 01 78 39 | ALL-AB-001 | Contract Requirements | N/A | Hold | 100% approved as-built set | N/A | Handover | Main Contractor | QAQC + Consultant |  |  |  |  | 0 |  |  |  | No | G5 | Open
Luxury Hotel QAQC | P06 Handover | All | All | Handover | O&M manuals and systems manual | HD-002 | DOC | HDO-002 | Final O&M and systems manual submission | Yes | 01 78 23 | ALL-OM-001 | Contract + WBDG Cx guidance | N/A | Hold | All systems manuals complete and indexed | N/A | Handover | Main Contractor | QAQC + Client |  |  |  |  | 0 |  |  |  | No | G5 | Open
Luxury Hotel QAQC | P06 Handover | All | All | Handover | Training and competency records | HD-003 | DOC | HDO-003 | Operator training plan and attendance/competency records | Yes | 01 79 00 | ALL-TRN-001 | Contract Requirements | N/A | Witness | Training completed by system and role | N/A | Handover | Main Contractor | QAQC + Operator |  |  |  |  | 0 |  |  |  | No | G5 | Open
Luxury Hotel QAQC | P06 Handover | All | All | Handover | Warranty and spare parts turnover | HD-004 | DOC | HDO-004 | Warranty matrix and spare parts register | Yes | 01 78 36 | ALL-WAR-001 | Contract Requirements | N/A | Review | Warranty start dates and spare list accepted | N/A | Final acceptance | Main Contractor | QAQC + Client |  |  |  |  | 0 |  |  |  | No | G5 | Open
Luxury Hotel QAQC | P06 Handover | All | All | Handover | Asset register and CMMS import file | HD-005 | DOC | HDO-005 | Asset tagging and CMMS upload sheet | Yes | 01 77 00 | ALL-AST-001 | Client FM Requirements | N/A | Review | 100% maintainable assets tagged and uploaded | N/A | Operational handover | Main Contractor | QAQC + FM |  |  |  |  | 0 |  |  |  | No | G5 | Open | Commonly forgotten